## таблица параметров
№ | Incident address | Length of the repaired section, m | Length of the section, m | Outside diameter, mm | Commissioning year | Wall thickness, mm | Residual pipeline wall thickness, mm, K1 | Previous incidents on the pipeline section, K2 | Soil corrosion activity, К3 | Flooding (traces of flooding) of the channel, K4 | Intersections with communications, K5 | Duration of incident resolution, h | Service life, years | Residual pipeline wall thickness, % | K1 | K2 | K3 | K4 | K5 | Involved features | Failure rate, 1/km*h | koef α | Practical Ki-values
1 | п. Октябрьский, ул. Ульяновская, д. 7 | 3 | 60 | 150 | 1980 | 4.5 | 2.75 | yes | low | no | no | 7 | 44 | 38.8889 |  |  | 1 | 1 | 1 | K1, K2 | 4.3241e-05 | 1.6091 | 1.1689
2 | п. Первомайский, пер. Садовый, д. 1 | 2 | 80 | 100 | 1983 | 3.5 | 1.75 | no | low | no | no | 4 | 41 | 50 |  | 1 | 1 | 1 | 1 | K1 | 3.4803e-05 | 1.5662 | 1.1418
3 | п. Пятисотенный, ул. Гагарина | 6 | 170 | 100 | 1985 | 3.5 | 2.5 | yes | high | no | yes | 10 | 39 | 28.5714 |  |  |  | 1 |  | K1, K2, K3, K5 | 1.7218e-05 | 1.3761 | 1.0124
4 | ул. Калинина 29, около ПУ-32 | 20 | 120 | 89 | 1978 | - | - | no | low | no | no | - | 46 | 0 |  | 1 | 1 | 1 | 1 | K1 | 2.068e-05 | 1.3968 | 1.0273
5 | пр. Сурова, 4, Авиастроительный р-н | 1 | 45 | 219 | 1987 | 8.5 | 7.1 | no | low | no | no | - | 37 | 16.4706 |  | 1 | 1 | 1 | 1 | K1 | 6.8562e-05 | 1.793 | 1.277
6 | р.п. Новая Майна центральная теплотрасса на жил.поселок ф273 | 72 | 250 | 273 | 1976 | 9 | 4 | yes | low | yes | no | 0.66667 | 48 | 55.5556 |  |  | 1 |  | 1 | K1, K2, K4 | 9.5129e-06 | 1.1804 | 0.85897
7 | р.п. Новая Майна ул Маширина | 1 | 150 | 108 | 1976 | 4 | 2.5 | yes | low | no | yes | 75 | 48 | 37.5 |  |  | 1 | 1 |  | K1, K2, K5 | 1.5855e-05 | 1.3179 | 0.96921
8 | р.п. Новая Майна ул. Микрорайон, д.4 | 5 | 40 | 108 | 1976 | 4 | 2.5 | yes | low | yes | no | 8 | 48 | 37.5 |  |  | 1 |  | 1 | K1, K2, K4 | 5.9456e-05 | 1.6739 | 1.2083
9 | р.п. Новая Майна ул. Микрорайон,10 до Микрорайон,9 | 1 | 100 | 219 | 1976 | 6 | 2.5 | yes | low | no | no | - | 48 | 58.3333 |  |  | 1 | 1 | 1 | K1, K2 | 2.3782e-05 | 1.4271 | 1.0488
10 | р.п. Новая Майна центральная теплотрасса до ул. Микрорайон,д.10 | 1 | 50 | 219 | 1976 | 6 | 2 | yes | low | no | no | - | 48 | 66.6667 |  |  | 1 | 1 | 1 | K1, K2 | 4.7565e-05 | 1.6138 | 1.1717
11 | р.п. Новая Майна до Микрорайон, 28 | 1 | 100 | 159 | 1976 | 4.5 | 2.5 | yes | low | no | no | - | 48 | 44.4444 |  |  | 1 | 1 | 1 | K1, K2 | 2.3782e-05 | 1.4271 | 1.0488
12 | р.п. Новая Майна Микрорайон, 10 до Микрорайон,8 | 2 | 150 | 133 | 1976 | 4 | 2.5 | yes | low | no | yes | - | 48 | 37.5 |  |  | 1 | 1 |  | K1, K2, K5 | 1.5855e-05 | 1.3179 | 0.96921
13 | р.п. Новая Майна ул. Микрорайон,22 | 1 | 100 | 108 | 1976 | 4 | 2 | no | low | no | no | - | 48 | 50 |  | 1 | 1 | 1 | 1 | K1 | 2.3782e-05 | 1.4271 | 1.0488
14 | с.Русский Мелекесс, ул. Совхозная,13 | 6 | 100 | 76 | 1969 | 3.5 | 3 | yes | low | no | yes | - | 55 | 14.2857 |  |  | 1 | 1 |  | K1, K2, K5 | 2.0756e-05 | 1.369 | 1.0072
15 | с.Русский Мелекесс, ул. Совхозная,1 | 5 | 40 | 76 | 1969 | 3.5 | 3 | yes | low | no | yes | - | 55 | 14.2857 |  |  | 1 | 1 |  | K1, K2, K5 | 5.1889e-05 | 1.6057 | 1.1667
16 | с.Русский Мелекесс, Школа | 5 | 30 | 76 | 1969 | 3.5 | 3 | yes | low | no | no | - | 55 | 14.2857 |  |  | 1 | 1 | 1 | K1, K2 | 6.9185e-05 | 1.68 | 1.2119
17 | р.п. Мулловка ,ул. Некрасова 01.10.2016г. | 5 | 5 | 57 | 1980 | 3.5 | 1.25 | no | low | yes | no | 8 | 44 | 64.2857 |  | 1 | 1 |  | 1 | K1, K4 | 0.00051889 | 2.2973 | 1.5249
18 | р.п.п Мулловка, ул. Клубная 02.10.2016г. | 2 | 2 | 57 | 1980 | 3.5 | 1.25 | no | low | yes | no | 8 | 44 | 64.2857 |  | 1 | 1 |  | 1 | K1, K4 | 0.0012972 | 2.5511 | 1.6297
19 | р.п.п Мулловка, ул. Клубная 03.10.2016г. | 15 | 15 | 57 | 1980 | 3.5 | 1.25 | no | low | yes | no | 8 | 44 | 64.2857 |  | 1 | 1 |  | 1 | K1, K4 | 0.00017296 | 1.9931 | 1.3828
20 | р.п. Мулловка, ул .Физкультурная С/К Текстильщик 07.10.2016г | 15 | 15 | 40 | 1980 | 2.5 | 1.25 | no | low | yes | no | 8 | 44 | 50 |  | 1 | 1 |  | 1 | K1, K4 | 0.00017296 | 1.9931 | 1.3828
21 | р.п. мулловка, ул. Физкультурная 13.10.2016г | 12 | 12 | 57 | 1980 | 3.5 | 1.25 | no | low | yes | no | 8 | 44 | 64.2857 |  | 1 | 1 |  | 1 | K1, K4 | 0.0002162 | 2.0549 | 1.4134
22 | р.п. Мулловка, ул. Мичурина 3 22.11.2016г. | - | - | 40 | 1980 | 2.5 | 1.25 | no | low | yes | no | 8 | 44 | 50 |  | 1 | 1 |  | 1 | K1, K4 | 2.5944e-05 | 1.4677 | 1.0768
23 | ул.Кузоватовская 29а | 3.4 | 66 | 57 | 1976 | 3.5 | 3 | no | low | no | no | 1 | 48 | 14.2857 |  | 1 | 1 | 1 | 1 | K1 | 3.6034e-05 | 1.539 | 1.1243
24 | ул.Кузоватовская 40 а | 3.5 | 22 | 89 | 1974 | 4 | 4 | no | low | no | no | 1.08 | 50 | 0 |  | 1 | 1 | 1 | 1 | K1 | 0.00010378 | 1.8116 | 1.2874
25 | ул.Федерации 5 | 0.6 | 74.5 | 219 | 1993 | 8.5 | 6 | no | low | no | no | 5.58 | 31 | 29.4118 |  | 1 | 1 | 1 | 1 | K1 | 4.9429e-05 | 1.7602 | 1.2586
26 | б.Пластова 6 | 40 | 182 | 108 | 1990 | 4 | 2.25 | no | low | no | no | 21.58 | 34 | 43.75 |  | 1 | 1 | 1 | 1 | K1 | 1.8448e-05 | 1.4263 | 1.0482
27 | ул.Рябикова 31 | 30.57 | 38 | 57 | 1983 | 3.5 | 3 | no | low | no | no | 2.5 | 41 | 14.2857 |  | 1 | 1 | 1 | 1 | K1 | 7.327e-05 | 1.7773 | 1.2682
28 | ул.Промышленная 38 | 11.87 | 94.4 | 273 | 1974 | 7 | 6 | no | low | no | no | 4 | 50 | 14.2857 |  | 1 | 1 | 1 | 1 | K1 | 2.4185e-05 | 1.4244 | 1.0469
29 | ул.Кирова 40 | 3 | 14 | 89 | 1965 | 4 | 4 | no | low | no | no | 3.25 | 59 | 0 |  | 1 | 1 | 1 | 1 | K1 | 0.0001382 | 1.8389 | 1.3023
30 | ул.Набережная реки Свияга 106 | 5 | 25 | 57 | 1993 | 3.5 | 3 | no | low | no | no | 5.5 | 31 | 14.2857 |  | 1 | 1 | 1 | 1 | K1 | 0.0001473 | 2.1038 | 1.4369
31 | ул.Гончарова 1 в | 1 | 19 | 108 | 1961 | 4 | 2.25 | no | low | no | no | 3.08 | 63 | 43.75 |  | 1 | 1 | 1 | 1 | K1 | 9.5368e-05 | 1.7291 | 1.2408
32 | ул.Камышинская 17 | 2 | 32.2 | 159 | 1986 | 4.5 | 4 | no | low | no | no | 5.58 | 38 | 11.1111 |  | 1 | 1 | 1 | 1 | K1 | 9.3295e-05 | 1.8733 | 1.3208
33 | ул.Кирова 36 | 6 | 11.35 | 57 | 1965 | 3.5 | 3 | no | low | no | no | 4.29 | 59 | 14.2857 |  | 1 | 1 | 1 | 1 | K1 | 0.00017047 | 1.892 | 1.3308
34 | Ввод первый переулок Полтавский,5 ТК-8а кв.12. | 3 | 20 | 80 | 1965 | 4 | 3 | no | low | no | no | 3 | 59 | 25 |  | 1 | 1 | 1 | 1 | K1 | 9.6742e-05 | 1.7486 | 1.252
35 | Ул.Герасимова кв.10 п.УЗТС от ТК-6 до Т-9 | 17 | 22 | 150 | 1975 | 4.5 | 4.5 | no | low | no | no | 3.5 | 49 | 0 |  | 1 | 1 | 1 | 1 | K1 | 0.0001059 | 1.823 | 1.2936
36 | Ввод Западный бульвар,13 ТК-15 | 4 | 135 | 100 | 1965 | 4 | 3 | no | low | no | no | 3 | 59 | 25 |  | 1 | 1 | 1 | 1 | K1 | 1.4332e-05 | 1.2653 | 0.92847
37 | Повреждение подающего трубопровода между ТК-17 и ТК-18 М-12 по ул. Матросова | 3 | 32.5 | 700 | 1970 | 9 | 7 | no | low | yes | no | 6 | 54 | 22.2222 |  | 1 | 1 |  | 1 | K1, K4 | 6.5046e-05 | 1.6684 | 1.205
38 | Ул.Октябрьская,53-55 | 2 | 51.5 | 100 | 1970 | 4 | 3 | no | low | no | no | 3.5 | 54 | 25 |  | 1 | 1 | 1 | 1 | K1 | 4.1048e-05 | 1.5488 | 1.1307
39 | Московское шоссе,39 ТК-19 кв.12 | 3 | 55 | 80 | 1965 | 4 | 3 | no | low | no | no | 3 | 59 | 25 |  | 1 | 1 | 1 | 1 | K1 | 3.5179e-05 | 1.4926 | 1.0936
40 | Повреждение подающего трубопровода в ТК-115 А между НС №5 и Т-122 М-13 по ул. Карла Маркса | 6 | 101 | 600 | 1977 | 8 | 6.5 | no | low | no | no | 5 | 47 | 18.75 |  | 1 | 1 | 1 | 1 | K1 | 2.4048e-05 | 1.434 | 1.0536
41 | Повреждение подающего трубопровода в корпусе компенсатора в ТК-25 М-12 по ул. Бебеля | 1 | - | 400 | 1970 | 9 | 6.5 | no | low | no | no | 4 | 54 | 27.7778 |  | 1 | 1 | 1 | 1 | K1 | 2.114e-05 | 1.3765 | 1.0127
42 | Повреждение подающего трубопровода между Т-2 и ТК-7 Кв-18 по ул. Пушкарева,20 | 8 | 318 | 300 | 1970 | 9 | 6.5 | no | low | no | no | 3.5 | 54 | 27.7778 |  | 1 | 1 | 1 | 1 | K1 | 6.6478e-06 | 1.076 | 0.76641
43 | Ул.Гончарова от ТК-24 до ТК-73 подача | 22 | 349 | 300 | 1974 | 9 | 6.5 | no | low | yes | no | 4 | 50 | 27.7778 |  | 1 | 1 |  | 1 | K1, K4 | 6.5418e-06 | 1.0767 | 0.76707
44 | Повреждение подающего трубопровода между ТК-128А и ТК-128 М-13 по ул. Лесная | 7 | 103.5 | 700 | 1977 | 9 | 8 | no | low | yes | no | 34 | 47 | 11.1111 |  | 1 | 1 |  | 1 | K1, K4 | 2.3467e-05 | 1.4273 | 1.049
45 | Повреждение подающего трубопровода в Т-4 на отпайке от М-10 к ЦТП «Университет», ул Минаева | 1 | - | 200 | 1967 | 6 | 3 | no | low | no | no | 3 | 57 | 50 |  | 1 | 1 | 1 | 1 | K1 | 2.0027e-05 | 1.3547 | 0.99674
46 | г.Инза, ул.Парковая,7 | 3 | 30 | 57 | 1989 | 3.5 | 1.4 | yes | low | no | no | 3 | 35 | 60 |  |  | 1 | 1 | 1 | K1, K2 | 0.00010872 | 1.9518 | 1.3619
47 | г.Инза, ул.Красных бойцов,24 | 32 | 32 | 27 | 1987 | 2.5 | 1.3 | no | low | yes | yes | 5 | 37 | 48 |  | 1 | 1 |  |  | K1, K4, K5 | 9.6415e-05 | 1.8932 | 1.3314
48 | г.Инза, ул.Шоссейная, 74 | 25 | 25 | 159 | 2007 | 4.5 | 1.8 | yes | low | no | no | 3 | 17 | 60 |  |  | 1 | 1 | 1 | K1, K2 | 0.0002686 | 2.9037 | 1.7591
49 | г.Инза, ул.Труда, 27 | 4 | 30 | 108 | 2012 | 4 | 1.4 | yes | low | yes | yes | 3 | 12 | 65 |  |  | 1 |  |  | K1, K2, K4, K5 | 0.0003171 | 4.0409 | 2.0896
50 | р.п.Кузоватово, котельная №1, участок теплотрассы от ТК№17 до ТК№18 | 20 | 80 | 110 | 1982 | 4 | 1.2 | yes | low | no | no | 6 | 42 | 70 |  |  | 1 | 1 | 1 | K1, K2 | 3.3975e-05 | 1.5534 | 1.1336
51 | ул.Зеленая д.7 до ул.Зеленая д.11 | 10 | 200 | 100 | 1970 | 4 | 1.25 | yes | low | yes | no | 24 | 54 | 68.75 |  |  | 1 |  | 1 | K1, K2, K4 | 1.057e-05 | 1.1965 | 0.87251
52 | ул.Зеленая д.5 | 22 | 140 | 57 | 1976 | 3.5 | 1.25 | yes | low | yes | no | 0.33333 | 48 | 64.2857 |  |  | 1 |  | 1 | K1, K2, K4 | 1.6987e-05 | 1.3365 | 0.9832
53 | пл.Ленина, 1 - пл. Ленина, 3 | 15 | 173 | 150 | 1967 | 4.5 | 2.5 | yes | high | yes | yes | 4 | 57 | 44.4444 | [5 empty] | K1, K2, K3, K4, K5 | 1.1576e-05 | 1.2146 | 0.88756
54 | ул.Калинина, 67 - ул. Калинина, 71 | 3 | 40 | 40 | 1997 | 2.5 | 1.75 | yes | low | no | no | 3 | 27 | 30 |  |  | 1 | 1 | 1 | K1, K2 | 0.0001057 | 2.0749 | 1.4231
55 | ул. Калинина,79 - ул. Л.Толстого, 99а | 6 | 50 | 89 | 1974 | 3.5 | 1.75 | yes | high | no | no | 4 | 50 | 50 |  |  |  | 1 | 1 | K1, K2, K3 | 4.5662e-05 | 1.5933 | 1.159
56 | р.п. Майна ул. Ленинская д.8 | 20 | 763 | 219 | 1984 | 8.5 | 4 | yes | low | no | no | 8 | 40 | 52.9412 |  |  | 1 | 1 | 1 | K1, K2 | 3.7403e-06 | 0.93453 | 0.62544